Tate Access Floors, Inc.

ContainAire Dual Sliding Doors

SECTION 09 69 00

Access Flooring Accessories

2.4	Accessories

Solid Doors:

Dual Sliding Doors:

Aisle containment Dual Sliding Doors shall be factory provided with the following specifications:

  - Finish: Frame shall be constructed of [clear anodize aluminum] [black anodize aluminum].

  - Dimensions: Dual Sliding Door frame shall have a height of 80” a width of 90.6” and a depth no greater than 4.85”

  - Design Features:

    - Viewing Panels shall be [6mm thick clear polycarbonate with edge sealing gaskets and meeting ASTM D-635 Listed] [6mm thick semi-transparent multiwall polycarbonate with edge sealing gaskets and meeting ASTM E-84 Listed and UL 94 Listed].

    - Aluminum frame shall be constructed from 6063-T6 alloy. Frame to be of no threshold design to minimize trip hazard

    - Double door system shall come packaged in pre-assembled sections with factory installed panels integrated door slide-locks and have factory installed perimeter compression gasket system to efficiently seal and minimize air leakage

    - Shall have ergonomic handles that reduce pinch points

    - Aisle containment doors shall be fully supported at the base of the frame and have the ability to attach to the equipment racks or other aisle containment components for lateral securement

    - [Double doors with multiwall polycarbonate are listed in UL file SA44425]