Tate Access Floors, Inc.

Multi-zone Opposed Blade Damper for DirectAire Specification

SECTION 09 69 00

ACCESS FLOORING ACCESSORIES

2.4 	Accessories

Airflow Controls:

Manual Dampers:

- Multi-zone Opposed Blade Damper for DirectAire: Damper shall be corner tab Hung beneath DirectAire panel and shall meet the following specifications:

- Finish & Material: Damper shall be manufactured and factory finished in clear anodized aluminum.

- Airflow Performance: Damper shall have the following airflow performance when installed with the following panels:

  - Each of three zones shall have 777 CFM or greater at 100% open and 71 CFM or less at 0% open when tested at 0.10” of static pressure when installed on an DirectAire 24” panel in a typical raised floor environment

- Design Features: Damper shall include the following features:

  - Shall be adjustable from 0-100%

  - Shall be adjustable without the removal of the airflow panel when used in conjunction with aforementioned panel.

  - Shall have three independently adjustable zones.

  - Shall be constructed of extruded aluminum