Tate Access Floors, Inc.

Drop-In Opposed Blade Damper

SECTION 09 69 00

ACCESS FLOORING

Part 2 – Products

Section 2.3   Panel Components

- The opposed blade damper shall have the following characteristics

  - Shall allow for field retrofit without the use of tools for installation

  - Shall be supported by the raised floor infrastructure

  - Shall be adjustable from 0-100%

  - Shall be adjustable without the removal of the airflow panel when used in conjunction with the Tate DirectAire airflow grate

  - Shall be constructed of extruded aluminum

- The opposed blade damper shall be have the following air flow characteristics when installed with a Tate DirectAire airflow grate

  - 1636 CFM or greater when 100% open, 915 CFM or greater when 50% open, and 234 CFM or less when 0% open when tested at 0.05” of static pressure when installed in a typical raised floor environment

  - 2331 CFM or greater when 100% open, 1296 CFM or greater when 50% open, and 326 CFM or less when 0% open when tested at 0.10” of static pressure when installed in a typical raised floor environment

  - 3339 CFM or greater when 100% open, 1838 CFM or greater when 50% open, and 466 CFM or less when 0% open when tested at 0.20” of static pressure when installed in a typical raised floor environment