Tate Access Floors, Inc.

Aisle Containment Hard Partition Kits

SECTION 09 69 00

Access Flooring Accessories

2.4	Accessories

Hard Partitions:

Aisle containment Hard Wall Partition shall be factory provided with the following specifications:

  - Finish: Frame shall be constructed of [clear anodize aluminum] [black anodize aluminum].

  - Dimensions: Hard Wall Partitions shall be of custom sizes, but no greater than 8’ high, 4’ wide, and 2” deep

  - Design Features:

    - Viewing Panels shall be [6mm thick clear polycarbonate with edge sealing gaskets and meeting ASTM D-635 Listed] [6mm thick semi-transparent multiwall polycarbonate with edge sealing gaskets and meeting ASTM E-84 Listed and UL 94 Listed].

    - Aluminum frame shall be constructed from 6063-T6 alloy. With frame designed to attach to adjoining Hard Wall Partitions

    - Hard Wall Partition kits shall come packaged in pre-assembled sections with factory installed panels integrated Mounting brackets for securement to racks and adjoining sections to be provided in package

    - Hard Wall Partitions shall be fully supported at the base of the frame and have the ability to attach to the equipment racks or other aisle containment components for lateral securement

    - [Hard wall partitions with multiwall polycarbonate are listed in UL file SA44425]