Tate Access Floors, Inc.

Containment Wall Partition

SECTION 13 21 33

Hot/Cold Aisle Containment Systems

# PART 1.  GENERAL

## 1.1 SUMMARY

A. Wall Partitions used for either hot or cold aisle containment.

## 1.2 SYSTEM DESCRIPTION

A. Custom sized for each application.

## 1.3 DESIGN REQUIREMENTS

A. Wall Partitions shall be individual aluminum framed panels with multiwall polycarbonate inserts. Panel multiwall inserts shall be Class A fire-rated material.

## 1.4 WARRANTY

A. Wall Partitions shall be warranted against defects in materials and workmanship for a one-year period for the first 12 months.

# PART 2. PRODUCTS

## 2.1 MANUFACTURERS

A. Basis of Design: Product specified is the Containment Wall Partition as manufactured by Tate Access Floors Inc.

B. Substitutions: Proposed substitutions must be approved prior to bidding.

## 2.2 GENERAL

A. Wall Partitions shall come packaged in pre-assembled sections with factory installed panels integrated Mounting brackets for securement to racks and adjoining sections to be provided in package.

B. Wall Partitions shall be fully supported at the base of the frame and have the ability to attach to the ceiling or other building structure for securement.

## 2.3 STRUCTURE

A. Frame shall be constructed of black, gray, or white painted aluminum.

B. Wall Partitions shall be of custom sizes, but no greater than 20’ high, 4’ wide, and 3.15” deep.

C. Viewing Panels shall be 6mm thick clear polycarbonate with edge sealing gaskets and meeting ASTM D-635 OR 8mm thick semi-transparent multiwall polycarbonate and meeting ASTM E-84 and UL 94 OR 16mm thick semi-transparent multiwall polycarbonate with edge sealing gaskets and meeting ASTM E-84 and UL 94 OR 3mm thick opaque black or white Dibond ACM with edge sealing gaskets and meeting ASTM E-84 Class A and UL 94 V-0 Rated.

D. Aluminum frame shall be constructed from 6063-T6 alloy. With frame designed to attach to adjoining Wall Partitions.

E.  Wall Partitions with multiwall polycarbonate are listed in UL file SA44425.

# PART 3. EXECUTION

## 3.1 INSTALLATION

- Install Wall Partitions in accordance with manufacturer's shop drawings and written instructions.

B. Wall Partitions shall be hanged from structural ceiling and secured with an angle bracket.

C. Installers shall provide appropriate installation hardware as defined by local code or the authority having jurisdiction.

## 3.2 ADJUSTING AND CLEANING

- Clean Wall Partitions with mild soap and water solution as needed.

END OF SECTION