SECTION 09 69 00

ACCESS FLOORING ACCESSORIES

2.4	ACCESSORIES

SOLID DOORS:

Dual Sliding Doors:

Aisle containment Dual Sliding Doors shall be factory provided with the following specifications:

  - Finish: Frame shall be constructed of [clear anodise aluminum] [black anodise aluminum].

  - Dimensions: Dual Sliding Door frame shall have a height of 203.2cm a width of 230.0cm and a depth no greater than 12.3cm”.

  - Design Features:

    - Viewing Panels shall be [6mm thick clear polycarbonate with edge sealing gaskets and meeting ASTM D-635 Listed] [6mm thick semi-transparent multiwall polycarbonate with edge sealing gaskets and meeting ASTM E-84 Listed and UL 94 Listed].

    - Aluminum frame shall be constructed from 6063-T6 alloy. Frame to be of no threshold design to minimise trip hazard.

    - Double door system shall come packaged in pre-assembled sections with factory installed panels integrated door slide-locks and have factory installed perimeter compression gasket system to efficiently seal and minimise air leakage.

    - Shall have ergonomic handles that reduce pinch points.

    - Aisle containment doors shall be fully supported at the base of the frame and have the ability to attach to the equipment racks or other aisle containment components for lateral securement.

    - [Double doors with multiwall polycarbonate are listed in UL file SA44425].