Tate Asia-Pacific Pty Ltd.

Tate Duo Data Centre Structural Ceiling

SECTION 09 54 00

SPECIALTY CEILINGS

PART 1. GENERAL

## 1.1 DESIGN REQUIREMENTS

A. Ceiling system shall be capable of directly supporting cable trays, utilities, light fixtures, HVAC registers and other accessories as indicated per area of work.

## 1.2 WARRANTY

A. Structural ceiling shall be warranted against defects in materials and workmanship for a period of 12 months from shipment.

# PART 2. PRODUCTS

## 2.1 MANUFACTURERS

A. Basis of Design: Product specified is the Tate Duo Structural Ceiling manufactured by Tate, Inc.

2.2 DESIGN FEATURES: Structural Ceiling grid shall include the following features:

A. 60 cm x 60 cm OR 60 cm x 120 cm centred grid system with continuous dual-threaded slot to accept both M10 OR M12 threads.

B. Main Runners and Structural Tees shall be notched on 60 cm centres for easy system installation and positive positioning of 60 cm and 120 cm Structural Tees.

C. Connectors to include ribs to align system with grid on 60 cm centre and prevent racking.

D. System is capable of fitting most commonly supplied 58.7cm2 OR 58.7 cm × 119.7 cm (+/- 3 mm) size ceiling tiles, light fixtures and HVAC registers.

E. 60 cm and 120 cm Structural Tees shall be cut back for vertical support through flange grid contact to Main Runners.

F. Connectors include M12 threaded turnbuckle connections

G. Connectors shall be constructed of high strength forged steel parts.

H. Internal Splice Connector shall be utilized for 3.6 m Main Runner splice locations.

I. Optional gasket: 2 mm thick x 9.5 mm closed cell polyethylene gasket tape shall be provided to improve leakage through system at various air pressures.

J. M10 button head Philips head screws with lock washer shall be utilized to secure connectors to Main Runners, Structural Tees, and Perimeter Angles.

K. System Weight:	i. 60 cm x 60 cm Grid: 52.6 N/m2

ii. 60 cm x 120 cm Grid: 43 N/m2

L. System shall be designed to allow for the installation of Tate Metal Ceiling tiles designed for the grid layout chosen.

M. System can be configured to allow for the use of off the shelf imperial tiles when required.

## 2.3 STRUCTURE

A. Structural Ceiling grid shall be installed with a Fixed OR a Floating perimeter angle condition option and on a 60 cm x 60 cm OR 60 cm x 120 cm grid supported with spacing of Custom Size connection to structure above.

B. Main Runners, Structural Tees, and Perimeter Angles shall be constructed of 6005-T5 extruded aluminium and have white, black, or silver painted aluminium finish.

C. Connectors: Field, Hanging, and Perimeter connectors shall be constructed of forged steel with corrosion resistant finish which is silver in colour.

D. Ceiling system shall be capable of supporting a uniform load up to 10.5 kN/m2.

E. Ceiling system shall be capable of a maximum static point load of 3.9 kN with standard duty connector.

F. Ceiling system shall be capable of a maximum static point load of 4.9 kN with heavy duty connector in line with turnbuckle connection to building structure.

G. Turnbuckle connection shall be capable of a maximum point load connection to building structure of 7.1 kN.

PART 3. EXECUTION

3.1 EXAMINATION

A. Verify ceiling support rod anchors are properly installed in structure above.

3.2 STRUCTURAL CEILING INSTALLATION

A. Structural Ceiling grid shall be installed on a 60 cm x 60 cm OR 60 cm x 120 cm grid supported with spacing of Custom Size connection to decking.

B. Grid spacing shall be defined by installation of 60 cm OR 120 cm Structural Tees.

C. Support Spacing shall be defined by positioning of turnbuckle connections offset from one another starting from one corner of the interior structural grid assembly and spaced evenly throughout.  Additional supports shall be provided as required along the perimeter and at any critical areas or as per seismic or code requirements or considerations.

D. Main Runners shall be installed on 120 cm centres and all main runners shall be parallel to one another. 120 cm Structural Tees shall be installed perpendicular to 3.6 m Main runners. Finally, a 60 cm Structural Tees shall be installed perpendicular to the 120 cm Structural Tees.

E. All work shall be coordinated with all other trades including but not limited to electrical, mechanical, fire protection and furniture.

3.3 PERIMETER INSTALLATION

A. Structural Ceiling grid shall be installed with a Fixed OR a Floating perimeter condition option.

B. Fixed perimeter installation: Perimeter Angles shall be mounted at level height to interior ceiling grid within 2.5 mm overall and .5 mm over any 3 m distance. Perimeter Angles shall be fastened to perimeter wall with appropriate wall type fasteners. Perimeter Angles can be field cut with non-ferrous carbide tipped blade. Joints shall fit with no more than 2 mm gaps.

C. Floating perimeter installation: Perimeter Angles shall be supported from structure at level height to interior ceiling grid within 2.5 mm overall and 1.5 mm over any 3 m distance.  Perimeter Angles shall be fastened to Main Runners and Structural Tees with perimeter connectors and suspended from structure above. Perimeter Angles shall be field cut with non-ferrous carbide tipped blade. Joints shall fit with no more than 3 mm gaps.

3.4. CLEANING

A. Inspect above and below installed ceiling system. Remove paint splatters and other spots, dirt, and debris. Touch-up scratches and mars of finish to match original finish.

END OF SECTION