Tate Asia-Pacific Pty Ltd.

Tate Strut Structural Grid

SECTION 09 54 00

SPECIALTY CEILINGS

- Structural Grid: Structural Ceiling grid shall be installed with [a Fixed] [a Floating] [no] perimeter angle condition option and on a [custom size] grid supported with spacing of [custom size] connection to structure above:

- Finish & Material:

  - Strut Main Runners and Structural Tees shall be constructed of Q235 or ASTM A283 galvanized steel and have [Galvanized] [Painted White] finish.

  - Light Structural infill shall be constructed of 6005-T5 extruded aluminium and have [Clear Anodized] [Painted White] [Painted Black] finish.

  - Connectors: All strut connector brackets shall be constructed of Q235 or ASTM 283 galvanized steel. All light structural connectors shall be constructed of high strength cast aluminium with corrosion resistant finish which is silver in colour.

- Performance: Ceiling system shall be capable of directly supporting cable trays, utilities, light fixtures, HVAC registers and other accessories as indicated per area of work.

  - Ceiling system shall be capable of supporting a uniform load up to [refer to datasheet for loading specification].

  - Ceiling system shall be capable of a maximum static point load of 1750lb (7.80kN) in the bottom slot of the strut.

  - Turnbuckle connection shall be capable of a maximum point load connection to building structure of 3500lb (15.60kN).

- Design Features: Structural Ceiling grid shall include the following features:

  - [Custom centre-to-centre strut spacing] centred strut system with [custom centre-to-centre infill spacing (e.g. 2’x4’) (e.g. 600mm x 1200mm)] Light Structural infill.

  - Strut Main Runners and Structural Tees shall be pre-drilled to required spacing for easy system installation and positioning of Light Structural infill pieces.

    - Light Structural to Tate Strut (LS to TS) Connectors shall be used to connect the Light Structural infill to Strut at pre-drilled holes along the Strut Main Runners and Structural Tees.

  - Light Structural infill shall be notched where necessary for positive positioning of Light Structural infill pieces.

    - Light Structural infill connectors to include ribs to align system with grid on correct centre and prevent racking.

  - System is capable of fitting [refer to datasheet for sizing] ceiling tiles, light fixtures and HVAC registers.

  - Strut Structural Tee flanges shall be coped back for vertical support through flange grid contact to Main Runners.

  - Light Structural infill pieces shall be coped back for vertical support through flange grid contact to adjacent pieces.

  - Connectors include 3/8”-16 or M10-1.5 threaded turnbuckle connections for Light Structural connectors if necessary.

  - Connectors include 1/2”-13 threaded turnbuckle connections for Strut connectors where necessary.

  - Connectors are available for perimeter installation.

  - 4-hole wrap around brackets and splice brackets shall be utilized for Main Runner splice locations.

  - 3-hole brackets shall be used at turnbuckle connections along Strut members that do not occur at Strut cross-intersections if permitted by the design.

  - Cross tee brackets shall be used at turnbuckle connections along Strut members that occur at Strut cross intersections if permitted by the design.

  - 3-hole brackets shall be utilized at Strut cross intersections if permitted by the design.

  - Light Structural connectors shall be constructed of high strength cast aluminium parts.

  - Strut connectors shall be constructed of Q235 or ASTM 283 galvanized steel.

  - 1/4”-20 button head Philips head screws with lock washer shall be utilized to secure Light Structural connectors to Light Structural infill pieces.

  - 1/2”-13 hex cap screws and channel nuts shall be utilized to secure Strut connectors to Strut Main Runners and Structural Tees.

  - [Optional gasket]

    - 1/8” thick x 3/8” (3.17mm x 9.52mm) closed cell polyethylene gasket tape shall be provided to improve leakage through system at various air pressures.

- Installation: Structural Ceiling grid shall be installed on a [custom] grid supported with spacing of [custom] connection to overhead structure:

  - Grid spacing shall be defined by installation of Light Structural Cross Tees and Strut Structural Tees.

  - Support Spacing shall be defined by positioning of 1/2” turnbuckle connections offset from one another starting from one corner of the interior structural grid assembly and spaced evenly throughout.  Additional supports shall be provided as required along the perimeter and at any critical areas or as per seismic or code requirements or considerations.

  - Strut Main Runners shall be installed on [custom] centres and all main runners shall be parallel to one another. Strut Structural Tees shall be installed perpendicular to Main Runners. Light Structural infill shall be installed in the open area between Strut members.

  - All work shall be coordinated with all other trades including but not limited to electrical, mechanical, fire protection and furniture.

- Perimeter Installation: Structural Ceiling grid shall be installed with [a Fixed] [a Floating] perimeter condition option.

  - Fixed perimeter installation: Perimeter Angles shall be mounted at level height to interior ceiling grid within 0.10” (2.5mm) overall and 0.06” (1.52mm) over any 10’ (3048mm) distance. Perimeter Angles shall be fastened to perimeter wall with appropriate wall type fasteners. Perimeter Angles can be field cut with non-ferrous carbide tipped blade. Joints shall fit with no more than .08” (2.03mm) gaps.

  - Floating perimeter installation: Perimeter Angles shall be supported from structure at level height to interior ceiling grid within 0.10” (2.5mm) overall and 0.06” (1.52mm) over any 10’ (3048mm) distance.  Perimeter Angles shall be suspended from structure above. Perimeter Angles shall be field cut with non-ferrous carbide tipped blade. Joints shall fit with no more than .125” (3.17mm) gaps.